Long Term Heat Storage Notes:  (for a 50,000 litre tank)

1.  We use a 10kW solar water heater, which provides 40kWh of heat energy per day in summer, 20kWh per day in winter, and 30kWh per day in Spring and in Autumn. 
(NOTE: 1kWh will heat 100 litres of water through 8.6 deg C, assuming no losses) 

2.  The tank will lose heat at the rate of 700 Watts continuously (see calculations below), which translates to 0.7 x 24 = 16.8 kWh lost per day.

3.  We use hot water for showers, etc. at the rate of 7kWh per day, year round.

4.  In winter, we also use the hot water in two 1kW radiator panels, for 10 hours each day.  That translates to a further loss of 20kWh per day in winter (for 90 days) 

5.  Right - now we do some sums. 
Divide the year up: Summer - 90 days, Winter - 90 days, Autumn and Spring - 90 days each.  We only use the radiators during the winter. 
Spring input: 30kWh x 90days = 2700kWh 
Spring losses: 16.8kWh x 90days = 1512kWh (at 700W continuously)

Spring hot water use: 7kWh x 90days = 630kWh
Spring NET input = 558kWh

Summer input: 40kWh x 90days = 3600kWh 
Summer losses: 16.8kWh x 90days = 1512kWh

Summer hot water use: 7kWh x 90days = 630kWh
Summer NET input = 1458kWh

Autumn NET input = 558kWh (same as Spring)

Winter input: 20kWh x 90days = 1800kWh 
Winter loss: 16.8kWh x 90days = 1512kWh(this is loss through tank walls)

Winter hot water use: 7kWh x 90days = 630kWh
Winter use: 20kWh x 90days = 1800kWh (used by radiator panels) 
Winter NET LOSS = 2142kWh NOTE:  This is a NET LOSS!

So, during Spring, Summer and Autumn, we get a total net gain of 2574kWh 
and during Winter, we get a total net loss of 2142kWh (NOTE: this is AFTER taking account of the loss due to radiation through the tank walls!) This gives a total net gain for the year, of 432kWh.

Now, we know that 1kWh raises the temperature of 100 litres of water though 8.6 deg C. 
Therefore, 2574kWh will raise the temp of the 50,000 litre tank through about 45 deg. C.   Which is MORE than we need.
This means that if the water starts off at 30degC in spring, it will get to 75degC by the beginning of winter, with a little leeway. 
In winter, it will lose 2142kWh over 90 days, which translates to a temperature drop of about 37 degrees by the end of winter, and the temperature ends up at around 30-40 degrees, to start the cycle over again.

# Heat Lost through the walls of the storage tank

Because the inside temperature of the tank is higher than the ambient temperature outside, heat will tend to flow through the walls of the tank at a rate determined by the difference in temperature between the inside and outside of the tank.  The rate of heat flow can be reduced by wrapping the tank with a suitable material which has a low “Thermal Conductivity”.  Thermal Conductivity is measured in units of Watts / (meters x Degrees C)  where meters is the thickness of the material, and Degrees is the difference in temperature across the insulating material.  From various sources, we find the Thermal Conductivity (“k”-value) for Polystyrene is 0.035 W/(metre x deg.), and for Polyurethane it is 0.025 W/(metre x deg.)

There is a formula for the Rate of Heat Flow (in Watts) through a thickness (d) of a material with thermal conductivity (k), total surface area (A), and with a temperature difference (t2 – t1)

This formula is:  Rate of Heat Flow = k x A x (t2 – t1) / d

Consider a tank 3.5m by 3.5m by 4m deep. (total volume = 49,000 litres)

Assume that the air temperature is 15 degrees C, the water temperature is 90 degrees C,  and that we are using 300mm (d = 0.3m) of polystyrene insulation (k = 0.035)

Total surface area A = 80.5 sq.m

Rate of Heat Flow = 0.035 x 80.5 x (90 – 15) / 0.3

= 704 Watts.

(Note:  This translates to a temperature drop of less than 0.5 degrees Centigrade per day if the tank is left without further heating.)